Consultant specification sheet Brazed heat exchangers

Product family: 	Brazed heat exchangers, BHE

Specific products:	Crazed heat exchanger, BHEto XXX--------------------------------------------
---B16, 18, 20, 30, 60, 110, 112, 200, 300, 400

Comment:		Standard version of products

General specifications:

- Supplier of the heat exchanger is Alfa Laval.

- Design of the heat exchanger shall be based on plate technology.

- Supplier of the heat exchanger shall control all steps in the chain; 
R&D, design, material purchase, plate pressing, brazing, testing, sales, after market etc.

- Supplier shall include all maintenance and installation manuals for the heat exchanger.

- Supplier shall be able to supply 2 and 3D drawings for the heat exchanger.

- All plates shall be single step pressed to secure uniform thickness of the plate and have no weak spots.

- All plates shall be pressed with herring bone or arrow pattern to give maximum turbulence, heat transfer capacity and contact points in the heat exchanger.

- Heat exchangers with asymmetric channels shall be selected where needed for pressure drop or flow reasons.

- All channel plates shall be with pressed alloy 316 stainless steel material.

- Pure copper (minimum 99,9%) shall be used as brazing material.

- The stainless steel plates should be brazed together in all contact points created between the adjacent plates as well as around the periphery of the plates to ensure a pressure resistant unit.

- Available pressure vessel codes from the supplier shall be; CE, KHK, KRA, CRN, UL, and ASME.

- Supplier shall test 100% of the heat exchangers prior to dispatch.

- All heat exchangers shall be tested in accordance with the specific pressure vessel code it has been produced for.

- All heat exchangers shall be pressure tested with air.

- All heat exchangers shall be leak tested with helium.

- All heat exchangers shall be produced in production facilities that are quality certified according to ISO 9001.

- All heat exchangers shall be produced in production facilities that are environmentally certified according to ISO 14001.

- All heat exchangers shall have an environmental product declaration in accordance with ISO 14021.

- Insulation for cooling or heating shall be offered by the supplier.

- All heat exchangers shall be marked with a sticker showing:

  - Manufacturer

  - Article number

  - Type

  - Manufacturing number

  - Manufacturing date

  - Max/min temperature

  - Max/min pressure

  - Test pressure

  - Volume

  - Fluid group

  - Part number

  - Pressure vessel stamp

  - Inlet/outlet orientation